## 1_Plant
Network | individual | opex | capex | opex_heat | opex_pump | opex_dis_loads | opex_dis_build | opex_chiller | opex_CT | opex_hex | capex_network | capex_pump | capex_dis_loads | capex_dis_build | capex_plant | capex_CT | capex_hex | total | plant_buildings | number_of_plants | supplied_loads | disconnected_buildings | has_loops | length | avg_diam
CBD_m | [0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 1.0, 0.0, 0.0, 0.0, 0.0] | 5853779.6853 | 1079362.3208 | 5772923.7713 | 27168.9104 | 0 | 0 | 45916.1365 | 4844.4938 | 2926.3733 | 39349.1275 | 13210.99 | 0 | 0 | 918322.7305 | 96889.8754 | 11589.5974 | 6933142.0061 | B006 | 1 | ahuaruscu |  | 0 | 1422.6338 | 0.2417
| [0.0, 0.0, 0.0, 0.0, 0.0, 1.0, 0.0, 0.0, 0.0, 0.0, 0.0, 1.0, 0.0, 0.0, 0.0, 0.0] | 5854450.608 | 1080820.4015 | 5773035.322 | 27728.033 | 0 | 0 | 45916.3593 | 4844.5203 | 2926.3733 | 38910.1344 | 15103.0775 | 0 | 0 | 918327.187 | 96890.4052 | 11589.5974 | 6935271.0094 | B006 | 1 | ahuaruscu |  | 1 | 1533.612 | 0.22015
|  | 670.9226 | 1458.0807 | 111.5507 | 559.1226 | [5 empty] | -438.9931 | 1892.0875 | [5 empty] | 2129.0033
|  | 0.01146% | 0.1349% | 0.001932% | 2.016% | [5 empty] | -1.128% | 12.53% | [5 empty] | 0.0307%
MIX_m | [0.0, 0.0, 0.0, 0.0, 0.0, 1.0, 1.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0] | 5028956.7563 | 931835.7996 | 4961033.8596 | 21175.5369 | 0 | 0 | 39467.9175 | 4077.8161 | 3201.6263 | 33111.6896 | 18248.0215 | 0 | 0 | 789358.3497 | 81556.321 | 9561.4178 | 5960792.5559 | B001 | 1 | ahuaruscu |  | 1 | 1809.8854 | 0.15788
| [0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 1.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0] | 5042587.2898 | 933162.838 | 4959873.5296 | 35969.9985 | 0 | 0 | 39464.7017 | 4077.4337 | 3201.6263 | 41613.3879 | 11145.3248 | 0 | 0 | 789294.0336 | 81548.674 | 9561.4178 | 5975750.1278 | B001 | 1 | ahuaruscu |  | 0 | 1382.1336 | 0.23676
|  | 13630.5335 | 1327.0384 | -1160.33 | 14794.4616 | [5 empty] | 8501.6983 | -7102.6968 | [5 empty] | 14957.5718
|  | 0.2703% | 0.1422% | -0.02339% | 41.13% | [5 empty] | 20.43% | -63.73% | [5 empty] | 0.2503%
RES_m | [0.0, 0.0, 0.0, 0.0, 0.0, 1.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 1.0] | 1606896.7159 | 439946.6866 | 1580712.1056 | 4908.0108 | 0 | 0 | 18809.1262 | 1598.2535 | 869.2198 | 20795.5037 | 6657.4897 | 0 | 0 | 376182.5247 | 31965.0695 | 4346.099 | 2046843.4025 | B010 | 1 | ahuaruscu |  | 1 | 1371.3396 | 0.11798
| [0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 1.0] | 1607488.3303 | 441673.9912 | 1580368.3862 | 5843.0044 | 0 | 0 | 18809.4302 | 1598.2896 | 869.2198 | 21357.8552 | 7815.641 | 0 | 0 | 376188.6037 | 31965.7923 | 4346.099 | 2049162.3214 | B010 | 1 | ahuaruscu |  | 0 | 1291.8552 | 0.12545
|  | 591.6143 | 1727.3046 | -343.7194 | 934.9936 | [5 empty] | 562.3515 | 1158.1513 | [5 empty] | 2318.9189
|  | 0.0368% | 0.3911% | -0.02175% | 16% | [5 empty] | 2.633% | 14.82% | [5 empty] | 0.1132%

## 1_Plant_for _report
Network | has_loops | total variable | opex_heat | opex_pump | capex_network | capex_pump | length [m] | avg_diam [m] | total | opex | capex
CBD_m | FALSE | 79729.0279 | 5772923.7713 | 27168.9104 | 39349.1275 | 13210.99 | 1422.6338 | 0.2417 | 6933142.0061 | 5853779.6853 | 1079362.3208
| TRUE | 81741.2448 | 5773035.322 | 27728.033 | 38910.1344 | 15103.0775 | 1533.612 | 0.22015 | 6935271.0094 | 5854450.608 | 1080820.4015
| Difference | 2012.2169 | 111.5507 | 559.1226 | -438.9931 | 1892.0875 | 110.9782 | -0.02155 | 2129.0033 | 670.9226 | 1458.0807
| Difference [%] | 2.462% | 0.001932% | 2.016% | -1.128% | 12.53% | 7.236% | -9.789% | 0.0307% | 0.01146% | 0.1349%
MIX_m | TRUE | 72535.248 | 4961033.8596 | 21175.5369 | 33111.6896 | 18248.0215 | 1809.8854 | 0.15788 | 5960792.5559 | 5028956.7563 | 931835.7996
| FALSE | 88728.7112 | 4959873.5296 | 35969.9985 | 41613.3879 | 11145.3248 | 1382.1336 | 0.23676 | 5975750.1278 | 5042587.2898 | 933162.838
| Difference | 16193.4631 | -1160.33 | 14794.4616 | 8501.6983 | -7102.6968 | -427.7518 | 0.078881 | 14957.5718 | 13630.5335 | 1327.0384
| Difference [%] | 18.25% | -0.02339% | 41.13% | 20.43% | -63.73% | -30.95% | 33.32% | 0.2503% | 0.2703% | 0.1422%
RES_m | TRUE | 32361.0042 | 1580712.1056 | 4908.0108 | 20795.5037 | 6657.4897 | 1371.3396 | 0.11798 | 2046843.4025 | 1606896.7159 | 439946.6866
| FALSE | 35016.5006 | 1580368.3862 | 5843.0044 | 21357.8552 | 7815.641 | 1291.8552 | 0.12545 | 2049162.3214 | 1607488.3303 | 441673.9912
| Difference | 2655.4964 | -343.7194 | 934.9936 | 562.3515 | 1158.1513 | -79.4844 | 0.0074672 | 2318.9189 | 591.6143 | 1727.3046
| Difference [%] | 7.584% | -0.02175% | 16% | 2.633% | 14.82% | -6.153% | 5.952% | 0.1132% | 0.0368% | 0.3911%
CBD_m | Branched | Looped | Difference | Difference [%]
length [m] | 1422.6338 | 1533.612 | 110.9782 | 7.236%
avg_diam [m] | 0.2417 | 0.22015 | -0.02155 | -9.789%
opex_heat [USD] | 5772923.7713 | 5773035.322 | 111.5507 | 0.001932%
opex_pump [USD] | 27168.9104 | 27728.033 | 559.1226 | 2.016%
capex_network [USD] | 39349.1275 | 38910.1344 | -438.9931 | -1.128%
capex_pump [USD] | 13210.99 | 15103.0775 | 1892.0875 | 12.53%
total variable cost [USD] | 79729.0279 | 81741.2448 | 2012.2169 | 2.462%
opex [USD] | 5853779.6853 | 5854450.608 | 670.9226 | 0.01146%
capex [USD] | 1079362.3208 | 1080820.4015 | 1458.0807 | 0.1349%
total [USD] | 6933142.0061 | 6935271.0094 | 2129.0033 | 0.0307%
MIX_m | Looped | Branched | Difference | Difference [%]
length [m] | 1809.8854 | 1382.1336 | -427.7518 | -30.95%
avg_diam [m] | 0.15788 | 0.23676 | 0.078881 | 33.32%
opex_heat [USD] | 4961033.8596 | 4959873.5296 | -1160.33 | -0.02339%
opex_pump [USD] | 21175.5369 | 35969.9985 | 14794.4616 | 41.13%
capex_network [USD] | 33111.6896 | 41613.3879 | 8501.6983 | 20.43%
capex_pump [USD] | 18248.0215 | 11145.3248 | -7102.6968 | -63.73%
total variable cost [USD] | 72535.248 | 88728.7112 | 16193.4631 | 18.25%
opex [USD] | 5028956.7563 | 5042587.2898 | 13630.5335 | 0.2703%
capex [USD] | 931835.7996 | 933162.838 | 1327.0384 | 0.1422%
total [USD] | 5960792.5559 | 5975750.1278 | 14957.5718 | 0.2503%
RES_m | Looped | Branched | Difference | Difference [%]
length [m] | 1371.3396 | 1291.8552 | -79.4844 | -6.153%
avg_diam [m] | 0.11798 | 0.12545 | 0.0074672 | 5.952%
opex_heat [USD] | 1580712.1056 | 1580368.3862 | -343.7194 | -0.02175%
opex_pump [USD] | 4908.0108 | 5843.0044 | 934.9936 | 16%
capex_network [USD] | 20795.5037 | 21357.8552 | 562.3515 | 2.633%
capex_pump [USD] | 6657.4897 | 7815.641 | 1158.1513 | 14.82%
total variable cost [USD] | 32361.0042 | 35016.5006 | 2655.4964 | 7.584%
opex [USD] | 1606896.7159 | 1607488.3303 | 591.6143 | 0.0368%
capex [USD] | 439946.6866 | 441673.9912 | 1727.3046 | 0.3911%
total [USD] | 2046843.4025 | 2049162.3214 | 2318.9189 | 0.1132%

## REPORT
MIX_m | Looped | Branched | Difference | Difference [%]
length [m] | 1810 | 1382 | -428 | -30.9%
avg_diam [mm] | 160 | 240 | 80 | 33.3%
opex_pump [USD] | 21176 | 35970 | 14794 | 41.1%
capex_network [USD] | 33112 | 41613 | 8502 | 20.4%
capex_pump [USD] | 18248 | 11145 | -7103 | -63.7%
total network related cost [USD] | 72535 | 88729 | 16193 | 18.3%